## Ductwork QAQC
# | Inspection Item | Pass | Fail | N/A | Comments / Notes
A. Submittals & Pre-Installation
1 | Submittals approved for all duct materials, sizes, gauges, fittings, and accessories per SMACNA
2 | Coordination confirmed with structural, electrical, sprinkler (avoid conflicts, enough space)
3 | Shop drawings include elevations, turning vanes, transitions, and damper access
B. Fabrication & Delivery
4 | Duct gauge and reinforcements confirmed based on size and pressure class
5 | All duct sections delivered clean, protected from weather and damage
6 | Duct insulation type, thickness, and vapor barrier verified
C. Installation Checks
7 | Ducts installed plumb, level, properly supported per SMACNA standards (hanger spacing, support for risers)
8 | Flexible duct lengths within limits (max 5–6 ft), and not kinked or compressed
9 | Turning vanes installed in elbows where required
10 | Volume dampers and access doors installed where shown and accessible
11 | Smoke/fire dampers installed with breakaway joints, sleeves, fusible links, and access
D. Testing & Commissioning
12 | Ductwork sealed (SMACNA Class A/B/C) per pressure class; leak test performed if required
13 | All diffusers, grilles, registers (DGRs) installed per reflected ceiling plan
14 | Duct insulation continuous and free of tears or exposed gaps
15 | Final cleaning completed prior to startup (negative air sweep or vacuum)
Code/Standard References:
• SMACNA Duct Construction Standards, ASHRAE 62.1, NBC 2019 Part 6, NECB
• NFPA 90A/90B, CSA F326 (Residential Air Distribution)
• Manufacturer Specs: Greenheck, Carnes, Price, Nailor, Loren Cook