## Exhaust System QAQC
# | Inspection Item | Pass | Fail | N/A | Comments / Notes
A. Submittals & Design Coordination
1 | Exhaust fan type, airflow, static pressure, voltage, and controls match schedule
2 | Duct material, gauge, insulation, and layout match submittals and SMACNA/NFPA standards
3 | Locations coordinated with architectural and structural elements, especially for garage or kitchen exhaust
B. Installation – Fans & Ducts
4 | Fan installed plumb and level, vibration-isolated, with backdraft damper if required
5 | Toilet and general exhaust duct slope to fan/roof per spec; sealed, firestopped
6 | Kitchen exhaust duct welded, sloped, continuous, grease-rated per NFPA 96
7 | Garage exhaust ductwork low-leakage and fire-smoke dampers accessible and tagged
8 | Roof/wall penetration flashed and sealed properly
C. Controls & Interlocks
9 | Fans interlocked with lights (toilet), hoods and make-up air (kitchen), or CO sensors (garage)
10 | CO/NO2 sensors installed per design, calibrated and interlocked to VFD/fans
11 | BAS/DDC points connected: fan status, alarms, airflow, override
D. Testing & Commissioning
12 | Airflow verified via TAB: each grille, hood, exhaust stack
13 | Kitchen hood pressure test (grease duct) and airflow balance completed
14 | Sound and vibration within acceptable limits
15 | AHJ inspection and fire authority clearance passed for grease hood (if applicable)
Code/Standard References:
• NFPA 90A, 96, SMACNA HVAC Duct Construction, ASHRAE 62.1, NECB 2020, NBC Part 6
• CSA C282 (Garage Fans/CO Interlocks), CAN/ULC-S649 (Grease Duct)
• Manufacturer Specs: Greenheck, Broan, CaptiveAire, Fantech, Loren Cook