## Hydronic Piping QAQC
# | Inspection Item | Pass | Fail | N/A | Comments / Notes
A. Submittals & Design Review
1 | Approved piping materials, sizing, insulation, and layout as per spec and drawings
2 | Isometric and spool drawings reviewed and coordinated with other trades
3 | Supports, guides, and anchors designed for thermal expansion and contraction
B. Installation – Piping & Valves
4 | Pipes installed level/plumb with correct slope (especially for air removal and drains)
5 | Isolation valves, strainers, unions, balancing valves, pressure/temp ports installed per plans
6 | Expansion loops or joints in place for long runs; no pipe stress or unsupported sections
7 | Flexible connectors installed at pumps and equipment
8 | Pipe identification labels and flow direction arrows in place
C. Equipment & Components
9 | Air separator, expansion tank, and automatic air vents installed correctly and operational
10 | Glycol feeder installed, filled, and relief protection in place (if applicable)
11 | Hydronic pumps installed with correct orientation, isolators, and accessible
D. Testing & Insulation
12 | Pressure test (typically 1.5x working pressure or per spec) witnessed and passed
13 | Flushing and chemical cleaning completed; water sample submitted for analysis
14 | System filled, de-aired, and flow direction confirmed
15 | Pipe insulation installed: correct thickness, vapor barrier sealed, no exposed gaps
E. Closeout
16 | As-built drawings submitted with piping routes, valves, and test data
17 | O&M manuals provided for pumps, feeders, valves, tanks, and flushing log
18 | AHJ and mechanical engineer signoff completed
Code/Standard References:
• ASHRAE 90.1, 55, NBC Part 6, NECB, CSA B51, B52, ANSI/ASHRAE 111 (Testing)
• Manufacturer Specs: Bell & Gossett, Taco, Armstrong, Grundfos, Flexcon, Victaulic