## IDF_MDF QAQC
# | Inspection Item | Pass | Fail | N/A | Comments / Notes
A. Room Conditions & Environmental Setup
1 | Room dimensions and ceiling height meet project specs and TIA-569-E guidelines
2 | HVAC installed to maintain 18–27°C with dedicated exhaust or cooling path
3 | Dust, water, plumbing, or unrelated equipment not present in room
B. Electrical & Grounding
4 | Dedicated 120V/208V 20A circuits for racks and IT gear installed per design
5 | Telecom Grounding Busbar (TGB) installed and bonded to main building ground per TIA-607-D
6 | Racks and ladder tray bonded to TGB with labeled #6 AWG minimum grounding wire
C. Racks, Cable Tray, and Termination Layout
7 | Equipment racks, ladder trays, wall fields, and cabinet layouts match shop drawings
8 | Fiber management systems and radius guides installed to spec
9 | Cable tray clearances maintained above and below for lighting, access, and ceiling grid
10 | Patch panels, termination blocks, and sleeves labeled per TIA-606 standards
D. Testing & Commissioning
11 | Fiber and copper cables within racks tested and terminated to rack elevations
12 | Power tested at each rack/cabinet PDU
13 | All equipment racks labeled and bolted securely to floor
E. Closeout & Documentation
14 | As-built layout, grounding diagram, elevation views, and labeling maps submitted
15 | Commissioning report, warranty documents, and asset registry submitted
Code/Standard References:
• ANSI/TIA-569-E, TIA-607-D, TIA-606-B, BICSI 002, CSA T530, NEC Article 800
• Manufacturer Specs: Chatsworth, Panduit, APC, Legrand, Middle Atlantic, Vertiv