## Louvers Vents QAQC
# | Inspection Item | Pass | Fail | N/A | Comments / Notes
A. Material Verification
1 | Louver/grille type and model matches mechanical/equipment schedule
2 | Louvers tested per AMCA/ASHRAE for free area, pressure drop, and water infiltration
3 | Finish (e.g., anodized, powder coat) and color match architectural elevations
4 | Accessories (bird screen, insect screen, blank-offs) received and match submittals
B. Rough Opening Prep
5 | Framed or masonry opening level, plumb, square
6 | Flashing, sill pan, and air barrier tie-ins prepped prior to install
7 | Coordination with mechanical and cladding trades complete before install
C. Installation of Louvers/Vents
8 | Louver frame fastened with anchors per manufacturer’s recommendation
9 | Sealant applied continuously around perimeter
10 | Bird/insect screens installed on interior side (unless specified otherwise)
11 | Interior duct or exhaust connections secured and aligned
D. Louver Banks / Architectural Grilles
12 | Multi-section louvers aligned for uniform reveals, depth, and spacing
13 | Continuous flashings and trim pieces installed between joined sections
14 | Decorative/architectural grilles aligned and secured against wind rattle
E. Final Inspection & Performance
15 | Free air opening confirmed per design (ducting or building automation reviewed if required)
16 | Water test or pressure performance tested (if required by consultant/spec)
17 | Manufacturer’s warranty and closeout documentation submitted
Code/Standard References:
• NBC Part 5 & 6, ASHRAE 62.1, NECB – Mechanical Ventilation
• AMCA 500-L, 500-D, 511 – Louver Testing Standards
• Manufacturer Specs: Airolite, Ruskin, Greenheck, Nailor, Titus
• Envelope Consultant Coordination Requirements