## Plumbing QAQC
# | Inspection Item | Pass | Fail | N/A | Comments / Notes
A. Submittals & Pre-Installation Review
1 | Approved submittals for piping, fittings, valves, insulation, and fixtures received and stamped
2 | Plumbing drawings coordinated with structural and architectural (penetrations, slopes, fixture locations)
3 | Code compliance verified: NPC, local AHJ amendments, backflow prevention, insulation R-values
B. Rough-In Verification – Water & Drainage
4 | Pipe routing and slope per NPC and design (2% minimum slope for drainage, per code)
5 | Cold and hot water pipes tested to minimum 100 psi for 2 hours, no leakage
6 | DWV tested with air (5 psi for 15 min) or water (10’ head for 15 min)
7 | Vents installed at all required locations with proper offsets and above flood rim
8 | Backflow preventers and isolation valves installed at designated risers or mechanical rooms
9 | Firestopping of penetrations installed and labeled
C. Fixture & Equipment Connection
10 | Fixtures installed level, anchored, and piped with approved materials and escutcheons
11 | Mixing valves, temperature limiters, and shutoffs installed per drawing
12 | Drainage connections properly vented and air gaps provided for indirect connections (e.g., dishwasher, ice maker)
13 | Hot water recirculation installed (if applicable) and flow verified
D. Final Inspection & Commissioning
14 | All valves, drains, and hose bibbs labeled and tagged
15 | All systems flushed, chlorinated (potable), and certified
16 | Fixture operation tested (fill/drain, flush, leak check) and clean
17 | As-built drawings submitted, O&M manuals turned over
18 | Final inspection passed by AHJ and certificate issued
Code/Standard References:
• National Plumbing Code (NPC 2020, Canada)
• CAN/CSA B64, CSA B125, ASTM D1785, NFPA 24
• Local Municipality/Province Regulations, LEED Water Efficiency Credits