## Structured Cabling QAQC
# | Inspection Item | Pass | Fail | N/A | Comments / Notes
A. Submittals & Design Review
1 | Cable type, rating (CMR/LSZH/Plenum), color, and termination types confirmed to match RFP/specs
2 | Approved shop drawings showing cable routes, IDF/MDF locations, and quantities
3 | Labeling scheme and numbering plan approved and consistent across drawings and racks
B. Backbone and Horizontal Cabling
4 | Cable supports (ladder tray, J-hooks, D-rings) installed with max spacing limits per BICSI/NEC
5 | Cables run with no kinks, sharp bends, or unpermitted splices
6 | Horizontal cable length does not exceed 90m from patch panel to outlet
7 | Fiber optic cable installed in innerduct with correct bend radius and pull tension
C. Terminations & Rack Setup
8 | Patch panels, jacks, and field terminations are punched down and labeled
9 | Patch cords installed with strain relief; no tight bends at connectors
10 | Rack layout neat with Velcro, lacing bars, cable managers installed
11 | Proper grounding and bonding provided for racks and cable tray
D. Testing & Commissioning
12 | Copper cable tested with Fluke/BERT for length, NEXT, return loss, and wiremap
13 | Fiber tested with OTDR for insertion loss and length
14 | Test reports submitted in PDF and original software formats
E. Closeout
15 | As-built drawings showing final cable routes and IDs provided
16 | O&M documentation including test results, warranties, and cut-sheets submitted
Code/Standard References:
• ANSI/TIA-568.3-D, TIA-606-B, NEC Chapter 8, BICSI 005, CSA T529
• Manufacturer Specs: Leviton, Belden, Panduit, Commscope, Corning, Hubbell, Siemon