## Sump Pump QAQC
# | Inspection Item | Pass | Fail | N/A | Comments / Notes
A. Submittals & Setup
1 | Pump type (storm, sanitary, effluent), GPM/head rating, and NEMA enclosure rating match mechanical schedule
2 | Submittals stamped and reviewed, including pump curves, float logic, and control panels
3 | Pit sizing and sump depth coordinated with civil and architectural elevations
B. Pit Construction & Equipment Installation
4 | Sump pit installed plumb and level, sealed, and protected against groundwater infiltration
5 | Concrete base installed under basin and slope provided to suction inlet
6 | Pump(s) secured and isolated from vibration; rails and removal guides in place for duplex systems
7 | Discharge piping installed with unions, check valves, and isolation valves
8 | Float switches, ultrasonic sensors, or pressure transducers mounted per manufacturer instructions
9 | Backflow prevention (if discharging to storm main) confirmed
C. Electrical & Controls
10 | Control panel installed and labeled; breaker rating and disconnect verified
11 | Float levels set to activate lead/lag pumps and alarm under high-level condition
12 | High water alarm with light and buzzer tested
13 | SCADA/BMS integration confirmed if required
D. Testing & Commissioning
14 | Wet test performed: simulate high water levels and verify pump sequence
15 | Flow rate and discharge confirmed (if testable)
16 | Pump startup log recorded, and manufacturer startup forms completed
17 | Final inspection passed by AHJ or mechanical engineer
Code/Standard References:
• NPC, CSA B128, CSA B73, ASTM C478 (Precast Pits)
• City of Calgary Drainage Design Standards, Local AHJ Inspection Requirements
• Manufacturer Specs: Liberty, Zoeller, Grundfos, Xylem, Myers, Pentair